Text for specification

Descrizione
AMBUS^®Panel
Base sezion. per fusibili cilindr.
10 x 38 / 1P
32 A / 690 V

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Omologazioni
IEC (CB), CSA, UL, CCC

Valori elettrici
corrente nominale (IEC):	32 A
tensione nominale (IEC) AC:	690 V

corrente nominale (UL):	30 A
tensione nominale (UL) AC:	600 V
tensione nominale (UL) DC:	600 V

AC-22B (400V)

power dissipation at full load of the item:	0.3 W

tensione nominale di isolamento U_i AC:	800 V
tensione di picco U_imp:	6 kV

SCCR:	100 kA

for fuse links as per IEC / EN 60269-2
with permitted rated power dissipations
up to max. 3W for gG/gL
up to max. 1.2W for aM

Connessioni
for applications acc. to IEC / EN :
1 wire: 
Cu 0,75 - 25 mm²
2 wires (of same cross-section): 
Cu 0,75 - 10 mm² 
flexible cables, directly or with wire-end ferrule
(flexible cables of max. cross-section may not fit when using wire-end ferrule)
Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

for applications acc. to UL / CSA :
only Cu cables acc. to UL 486E
1 wire: 
AWG 18 - AWG 8, Class B, Md 2,0 -2,5 Nm / 18 - 22 lb.in.
AWG 6 - AWG 4, Class C, Md 2,5 - 3,0 Nm / 22 - 26 lb.in.
2 wires (of identical cross-section): 
AWG 18 - AWG 8, Class B, Md 2,0 - 2,5 Nm / 18 - 22 lb.in. 
AWG 6, Class C, Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

Proprietà materiali
Corpo base:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Portafusibile:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
	
Viti di collegamento:
	screw +/- (PZ2), galvanized, chromized 

Miscellaneous 
large clamping range
holder for label

Brand 
Woehner or equivalent

Cod. art.
31110000