Text for specification

Descrizione
AMBUS^®Panel
Base sezion. per fusibili cilindr., per fus. extrarapidi
14 x 51 / 3P
50 A / 690 V

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Omologazioni
IEC (CB), CSA, UL, CCC

Valori elettrici
corrente nominale (IEC):	50 A
tensione nominale (IEC) AC:	690 V

corrente nominale (UL):	50 A
tensione nominale (UL) AC:	600 V
tensione nominale (UL) DC:	600 V

power dissipation at full load of the item:	2.7 W

tensione nominale di isolamento U_i AC:	800 V
tensione di picco U_imp:	6 kV

SCCR:	100 kA

for fuse links as per IEC / EN 60269-2 with permitted rated power dissipationsup to max. 5W for gG/gL up to max. 3W for aM for fuse links aR / gR / gRL under operation conditions up to max. 6.5W, for which at least 25mm² leads must be connected

Connessioni
morsetti a gabbia :
1,5 - 35 mm² / AWG 14 - AWG 2 
cavi flessibili, direttam. o con ferrula
C. serr. 2,5 - 3,0 Nm / 22 - 26 lb.in.

(cavi flessibili con ferrula potrebbero no più entrare, se scelti con sezione max.)

Proprietà materiali
Corpo base:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Portafusibile:
	temperature stability 140°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Viti di collegamento:
	screw +/- (PZ2), galvanized, chromized 

Miscellaneous 
large clamping range
 holder for label

Brand 
Woehner or equivalent

Cod. art.
31280000