Text for specification

Descrizione
SECUR^®60Classic PowerLiner
sezionatore per fusibili D0, montaggio su barre
per fusibili D01 e D02, con LED
E18 / 63 A /3P
60Classic

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Omologazioni
VDE, CCC

Valori elettrici
corrente nominale (IEC):	63 A
tensione nominale (IEC) AC:	400 V
tensione nominale (IEC) DC:	110 V

AC-23A (400 V)

DC-21B (48V) 1 pole
DC-21B (110V) 2 poles

power dissipation at full load of the item:	10.5 W

tensione nominale di isolamento U_i AC:	500 V
tensione di picco U_imp:	6 kV

LED indicates blown fuse, operating range: 110 - 400 V AC / DC

for fuse links and gauge rings as per DIN VDE 0636-3 IEC / HD 60269-3
utilisation category as per VDE 0638: AC22

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard.

There is a transfer of the potential from the busbars, through the LED units, to the terminals  when the fuse links are removed and the switching mechanismn is closed. 

Proprietà materiali
Involucro:
	resistenza alle temperature fino a 140°C,
	ignifugo secondo UL 94, 
	tenuta alle correnti di fuga CTI 225,
	Senza silicio, senza alogeni
Levetta di manovra:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200
Portafusibile:
	temperature stability 150°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 125,
	halogen-free
Copertura:
	temperature stability 125°C,
	fire behaviour UL 94 HB,
	creepage resistance CTI 200,
	halogen-free 
Viti di collegamento:
	screw +/- (PZ2), galvanized, chromized 

Brand 
Woehner or equivalent

Cod. art.
31525000