Text for specification

Descrizione
QUADRON®Panel
Base per fusibili cilindr.
Class J / 3P, morsetti 150 mm²
200 A / 600 V (41x146)

Norme
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016, Fuse system H

Omologazioni
CSA, UL

Valori elettrici

corrente nominale (UL):	200 A
tensione nominale (UL) AC:	600 V
tensione nominale (UL) DC:	600 V

power dissipation at full load of the item:	7.4 W

SCCR:	200 kA

for Class J fuses 110 - 200A as per UL 248-8 (41x146)

Connessioni
tunnel terminal with hole of 17,0 mm diameter

acc. to IEC / EN :
10 - 150 mm²
flexible cables, directly or with wire-end ferrule, 
solid and stranded round cables, 
Md 16 - 18 Nm

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

acc. to UL :
AWG 8 - MCM 300
stranded cables Class B acc. to UL 486E
142 - 160 lb.in.

Proprietà materiali
Corpo base:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Protezione contro contatto accidentale:
	temperature stability 125°C,
	fire behaviour UL 94 HB,
	creepage resistance CTI 200,
	halogen-free 
Viti di collegamento:
	screw M8, galvanized, chromized

Brand 
Woehner or equivalent

Cod. art.
33307000