Text for specification

Descrizione
QUADRON®60Classic
base sezion. per fus. NH2, 400 A, per barre, uscita in basso / alto
vite M10
60Classic

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Omologazioni
IEC (CB), UL, CCC

Valori elettrici
corrente nominale (IEC):	400 A
tensione nominale (IEC) AC:	690 V
tensione nominale (IEC) DC:	250 V

corrente nominale (UL):	400 A
tensione nominale (UL) AC:	600 V

AC-23B (400V)
AC-22B (500 V)
AC-21B (500 V)

power dissipation at full load of the item:	45.0 W

tensione nominale di isolamento Ui AC:	690 V
tensione di picco Uimp:	6 kV
tensione max. ammissibile (IEC) AC:	725 V
tensione max. ammissibile (IEC) DC:	262 V

SCCR:	100 kA

for fuse links IEC 60269-2-1 (I) / DIN VDE 0636-201 size 2 up to 34W power dissipation, with grip lugs under voltage

Schutzart IP30 frontseitig, im Anschlussbereich vom Einbau abhängig

Elektronische Sicherungsüberwachung:
- Zur Erkennung von Sicherungsausfällen mit Bemessungsspannung AC 100V bis AC 690V
- Keine Hilfsenergie erforderlich; Versorgung über Netzspannung
- Hilfskontakte potentialfrei
- LED- Blinkmelder (rot/grün)
- Testtaster
- Weitere Informationen unter Downloads / Datenblatt

Connessioni
Accessories:
Clamp connection:  Cu 120-240mm² s(r), f+AE; lam. Cu 21x1-14; 6-8Nm torque
single wedge clamp terminal: Cu, Al* 120-240mm² s(r), s(s), f, f+AE; 6-8 Nm torque
double wedge clamp terminal: Cu  2x 70-120mm² s(r), s(s), f+AE;  6-8Nm torque

*Connections are not maintenance-free if aluminium conductors are used.

Proprietà materiali
Corpo base:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Protezione contro contatto accidentale:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Coperchio:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Piastra adattatore:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Contatti:
	spring-loaded copper contacts, silver plated 
Viti di collegamento:
	screw M10, galvanized, chromized

Miscellaneous 
Disconnectors are equipped with arc chambers.
The shock protection is split into 2 for safe connection of the conductors.

Brand 
Woehner or equivalent

Cod. art.
33326000