Text for specification

Descrizione
CAPUS^®Panel
Sezionatore sottocarico per fusibili NH, 3p
viti M10, manovra nera
Gr. NH 2

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Omologazioni
IEC (CB)

Valori elettrici
corrente nominale (IEC):	400 A
tensione nominale (IEC) AC:	690 V

AC-23B (690V)
AC-22B (690V)
AC-21B (690V)

power dissipation at full load of the item:	109.0 W

tensione nominale di isolamento U_i AC:	1000 V
tensione di picco U_imp:	8 kV

Mechanical lifespan (switching operations) 7000

conv. therm. current in housing
400 A, horizontal installation (adjacent poles) encapsulated 504 x 378 x 302 mm
315 A, vertical installation (poles beneath each other) encapsulated 500 x 500 x 300 mm

Shock protection at front with terminal space cover IP20

for fuse links DIN 43620 size 2 up to 34W power dissipation

Connessioni
viti M10 :
C. serr. 25 - 31 Nm

Miscellaneous 
double-breaking main contacts,
visible separation sections,
user-independent switching,
voltage-free exchange of fuses
assembly and connection material contained in scope of delivery.

Brand 
Woehner or equivalent

Cod. art.
33339000