Text for specification

Descrizione
CAPUS®Panel
Sezionatore sottocarico, 3 poli
viti M12, manovra rossa
800 A

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Omologazioni
IEC (CB)

Valori elettrici
corrente nominale (IEC):	800 A
tensione nominale (IEC) AC:	500 V

AC-23B (500V)
AC-22B (500V)
AC-21B (500V)

power dissipation at full load of the item:	169.0 W

tensione nominale di isolamento Ui AC:	1000 V
tensione di picco Uimp:	12 kV
potere nominale di chiusura:	40 kA

Switching capacity/utilisation categories AC-23B (500V);  AC-22B (500V); AC-21B (500V)
Mechanical lifespan (switching operations) 2500
Rated short-circuit making capacity 40kA

conv. therm. current in housing
800A, horizontal installation (adjacent poles) encapsulated 756 x 378 x 482mm
800A, vertical installation (poles beneath each other) encapsulated 600 x 600 x 400mm

Shock protection at front with terminal space cover IP40

Connessioni
viti M12 :
C. serr. 36 - 44 Nm

Miscellaneous 
double-breaking main contacts, 
visible separation sections, 
user-independent switching, 
assembly and connection material contained in scope of delivery

Brand 
Woehner or equivalent

Cod. art.
33358000