Text for specification

Descrizione
QUADRON^®60Classic
Base per fusibili Class J, per barre, connessione in basso / alto
per fusibili Class J, 70 - 100 A (29 x 118)
3p, con morsetto a gabbia
60Classic

Norme
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016, Fuse system H

Omologazioni
UL

Valori elettrici

corrente nominale (UL):	100 A
tensione nominale (UL) AC:	600 V
tensione nominale (UL) DC:	600 V

power dissipation at full load of the item:	9.0 W

SCCR:	200 kA

do not use any fuse links with sharp-edged contact blades

System component: degree of protection IP30 at front as per DIN EN 60529, degree of protection near terminal depends on installation
adapter module: front side degree of protection IP20 as per DIN EN 60529 (finger-safe)

Connessioni
AWG 12 - AWG 2/0 stranded, equivalent 3,3 - 67,4 mm²
AWG 14 - AWG 10 solid, equivalent 215 - 5,3 mm²

Proprietà materiali
Corpo base:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Piastra adattatore:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Coperchio:
	resistenza alle temperature fino a 125°C, 
	ignifugo secondo UL 94, 
	tenuta alle correnti di fuga CTI 200

Miscellaneous 
the product is based on the UL approval in category IZLT2 also listed in category NMTR (file E123577)

CrossLink® adapter technology
Fast and safe conversion of the connection for top or bottom; the parts under voltage remain shock protected Simple and safe clicking into place and making contact
Safe connection through shock protection split into 2
Busbar supports for flat busbars can be mounted above each other

Brand 
Woehner or equivalent

Cod. art.
33402000