Text for specification

Descrizione
QUADRON^®185Power
Base verticale per fusibili NH 250 A
vite M10
Gr. NH 1
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Norme
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Valori elettrici
corrente nominale (IEC):	250 A
tensione nominale (IEC) AC:	690 V

power dissipation at full load of the item:	30.0 W
tensione di picco U_imp:	12 kV
tensione max. ammissibile (IEC) AC:	1000 V
resistenza al corto circuito con protezione tramite fusibili:	50 kA

for fuse links IEC 60269-2 / DIN VDE 0636-201 size 1 up to 23W power dissipation 

Connessioni
screw M12 :
Md 30 Nm

Proprietà materiali
Corpo base:
	resistenza alle temperature fino a 130°C,
	ignifugo secondo UL 94,
	tenuta alle correnti di fuga CTI 600,
	senza alogeni
Contatti:
	spring-loaded copper contacts, silver plated 
Protezione contro contatto accidentale:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200

Brand 
Woehner or equivalent

Cod. art.
33706000A