Text for specification

Descrizione
CRITO^®CrossBoard
modulo di connessione
150 mm², per alimentazione posteriore del CrossBoard
3p

Norme
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Omologazioni
UL

Valori elettrici
corrente nominale (IEC):	160 A
tensione nominale (IEC) AC:	690 V

corrente nominale (UL):	160 A
tensione nominale (UL) AC:	600 V
corrente d'impiego max. (IEC):	160 A

tensione nominale di isolamento U_i AC:	800 V
tensione di picco U_imp:	6 kV
tensione max. ammissibile (IEC) AC:	800 V
tensione max. ammissibile (IEC) DC:	800 V

resistenza nom. alla corrente di picco I_pk max.:	30 kA

SCCR: 65 kA with any DIVQ/7 circuit breaker 400 A / 480 V AC, 100 kA with JDDZ fuse Class J 400 A / 600 V AC 

Connessioni
Connecting circular conductors: 

35... 50 mm² / 2... 1/0 AWG 

4Nm / 35 lb in

70... 150 mm² / 2/0 AWG... 300 kcmil

6Nm / 53 lb in

35... 95 mm² flexible conductors, circular stranded conductors, flexible conductors with wire-end ferrules DIN 46228-1 max. 30 mm

120... 150 mm² flexible and circular stranded conductors

Connecting flexible conductors:

4x - 10x 15,5mm  x 0,8 mm

6Nm / 53 lb in  

Suitable for aluminium cables.
When using aluminium cables, observe the maintenance instructions.

Brand 
Woehner or equivalent

Cod. art.
01595000A