Text for specification

Descrizione
QUADRON®60Classic
base sezion. per fus. NH 00,160 A, per barre, uscita in basso / alto
morsetti a gabbia
versione speciale per sistemi barre 5p 
60Classic

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Omologazioni
IEC (CB), UL, VDE, CCC

Valori elettrici
corrente nominale (IEC):	160 A
tensione nominale (IEC) AC:	690 V
tensione nominale (IEC) DC:	440 V

corrente nominale (UL):	160 A
tensione nominale (UL) AC:	600 V

AC-21B (690V)
AC-22B (500V)
AC-20B (1000V) at pollution degree 2

visible information required if used at more than 690V AC or 160A: do not switch under load

DC specifications: 2 current paths (L1,L3) in series
DC-21B (220V)
DC-21B (440V/100A)
DC-22B (220V/63A)
DC-20B (1000V) at pollution degree 2

visible information required if used at more than 440V DC or 160A: do not switch under load

power dissipation at full load of the item:	17.7 W

tensione nominale di isolamento Ui AC:	800 V
tensione di picco Uimp:	6 kV
tensione max. ammissibile (IEC) DC:	800 V

SCCR:	100 kA

Entsprechend den angegeben AC- und DC- Schalteigenschaften und unter Berücksichtigung der Überlastbedingungen, sind gewisse Abstände zu geerdeten Metallteilen einzuhalten. Nähere Informationen auf Anfrage.

Bei Dauerbetrieb von mehreren Geräten nebeneinander ist der Bemessungsbelastungsfaktor nach VDE 0660 Teil 500 / EN60439-1, Tabelle 1 zu beachten.

System component: degree of protection IP30 at front as per DIN EN 60529, degree of protection near terminal depends on installation, adapter module: front side degree of protection IP20 as per DIN EN 60529 (finger-safe)

Connessioni
Box terminal:
1.5 - 70 mm² flexible cables, directly or with wire-end ferrules*, depending on contour of the lead 95 mm² could be connectable 
1.5 - 10 mm² solid round
16 - 70 mm² stranded round 
2x 10 mm², 2x 16 mm² and 2x 25 mm² flexible with wire-end ferrules, identical cables placed side by side, crimping square 
2x 10 - 35 mm² flexible identical cables placed side by side

lam. Cu. 9 - 13 mm wide 
terminal space 13 mm x 13 mm

(*flexible cables of maximum cross-section may not fit when using wire-end ferrule)

für Anwendungen nach UL :
  nur Cu-Leitungen stranded/solid nach UL 486E
  AWG 12 - AWG 2/0
  Md 5,0 - 6,0 Nm / 44 - 53 lb.in. 

Miscellaneous 
CrossLink® adapter technology
Fast and safe conversion of the connection for top or bottom; the parts under voltage remain shock protected
Simple and safe clicking into place and making contact
Safe connection through shock protection split into two
Busbar supports for flat busbars can be mounted above each other

Brand 
Woehner or equivalent

Cod. art.
33075000