Text for specification

Descrizione
QUADRON®30Compact
base sezion. per fus. NH000, per montaggio su barre, 125 A, uscita in basso / alto
morsetti a gabbia
30Compact 3P

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Valori elettrici
corrente nominale (IEC):	125 A
tensione nominale (IEC) AC:	690 V
tensione nominale (IEC) DC:	440 V

AC-21B (690 V / 80 A)
AC-22B (400 V / 125 A)

power dissipation at full load of the item:	10.5 W

tensione nominale di isolamento Ui AC:	800 V
tensione di picco Uimp:	6 kV
tensione max. ammissibile (IEC) DC:	800 V

In accordance with the specified AC and DC switching properties and in consideration of the overload conditions, certain distances to earthed metal parts are to be adhered to. detailed information upon inquiry

When several devices are used side-by-side in continuous operation, the rated load factor specified in IEC / EN 61439-1, Table 1, must be observed.

Connessioni
box terminal:
1.5 - 50 mm² flexible and flexible with wire-end ferrules*
2.5 - 50 mm² flexible
2.5 - 16 mm² solid round
2.5 - 50 mm² stranded round

Terminal space 10 mm x 10 mm

(*flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Proprietà materiali
Involucro:
	temperature stability 125°C,
	self-extinguishing in acc. to UL 94,
	creepage resistance CTI 600,
	halogen-free
Coperchio:
	resistenza alle temperature fino a 125°C, 
	ignifugo secondo UL 94,
	tenuta alle correnti di fuga CTI 600
Contatti:
	spring-loaded copper contacts, silver plated 

Miscellaneous 
only 49.5 mm wide rotatable for connection at bottom or top 

Brand 
Woehner or equivalent

Cod. art.
33801000A