Text for specification

Descrizione
QUADRON^®185Power
Base sezion. verticale per fusibili NH, 160 A
Gr.  00, sez. contemp. , con monitoraggio fus.
flat version with screw M8
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Omologazioni
IEC (CB), CCC

Valori elettrici
corrente nominale (IEC):	160 A
tensione nominale (IEC) AC:	400 V

AC-23B 160A/400V
AC-22B 160A/500V 

power dissipation at full load of the item:	23,0 W

tensione nominale di isolamento U_i AC:	400 V
tensione di picco U_imp:	4 kV

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

Degree of protection IP20 at front, degree of protection near terminal depends on installation

Connessioni
viti M8 : 
C. serr. 12 - 14 Nm

Proprietà materiali
Corpo base:
	resistenza alle temperature fino a 130°C,
	ignifugo secondo UL 94,
	tenuta alle correnti di fuga CTI 600,
	senza alogeni
Contatti:
	spring-loaded copper contacts, silver plated 
Protezione contro contatto accidentale:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Coperchio:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Viti di collegamento:
	screw M8, galvanized, chromized 

Miscellaneous 
Self-closing inspection holes are available in the cover.
Cover can be locked when closed.

Brand 
Woehner or equivalent

Cod. art.
33724000A