Text for specification

Descrizione
QUADRON^®185Power
Base sezion. verticale per fusibili NH, 160 A
Gr. 00, sez. singolarm. 
morsetti a gabbia 70mm²
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Omologazioni
IEC (CB), CCC

Valori elettrici
corrente nominale (IEC):	160 A
tensione nominale (IEC) AC:	690 V

AC-23B 160A/400V
AC-22B 160A/500V 

DC-20B
max. voltage between the fuses: 1000V
visible information required: Do not switch under load.

power dissipation at full load of the item:	23,0 W

tensione nominale di isolamento U_i AC:	1000 V
tensione di picco U_imp:	8 kV

Degree of protection IP20 at front, degree of protection near terminal depends on installation

Connessioni
Box terminal:
1,5 -70mm² flexible cables, directly or with wire-end ferrules*, depending on contour of the insulated lead 95mm² could be connectable
1,5 -10mm² solid round
16 -70mm² stranded round
2x10mm², 2x16mm² and 2x25mm² flexible with wire-end ferrules, identical cables placed side by side, crimping square
2x 10-35mm² flexible identical cables placed side by side

lam. Cu. 9-13 mm wide
terminal space 13mm x 13mm

(*flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Proprietà materiali
Corpo base:
	resistenza alle temperature fino a 130°C,
	ignifugo secondo UL 94,
	tenuta alle correnti di fuga CTI 600,
	senza alogeni
Contatti:
	spring-loaded copper contacts, silver plated 
Protezione contro contatto accidentale:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Coperchio:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
connection:
	box terminal 95mm², galvanized, chromized 

Miscellaneous 
Self-closing inspection holes are available in the cover.
Cover can be locked when closed.

Brand 
Woehner or equivalent

Cod. art.
33775000A