Text for specification

Descrizione
QUADRON^®Panel
Base sezion. per fus. NH00, 160 A, per pannello
vite M8, con protezione corta

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Omologazioni
IEC (CB), UL, CCC

Valori elettrici
corrente nominale (IEC):	160 A
tensione nominale (IEC) AC:	690 V
tensione nominale (IEC) DC:	440 V

corrente nominale (UL):	160 A
tensione nominale (UL) AC:	600 V

AC-23B (400V)
AC-23B (500V/125A)
AC-22B (690V)
AC-21B (690V)
AC-20B (1000V) at pollution degree 2

visible information required if used at more than 690V AC: do not switch under load

DC specifications: 2 current paths (L1,L3) in series
DC-22B (220V)
DC-22B (440V/125A)
DC-21B (440V)
DC-20B (1000V) at pollution degree 2

visible information required if used at more than 440V DC: do not switch under load

power dissipation at full load of the item:	7,0 W

tensione nominale di isolamento U_i AC:	800 V
tensione di picco U_imp:	6 kV
tensione max. ammissibile (IEC) DC:	800 V

SCCR:	100 kA

In accordance with the specified AC and DC switching properties and in consideration of the overload conditions, certain distances to earthed metal parts are to be adhered to. Further information on request.
When used as a disconnector, the spacings can be ignored.

Degree of protection IP30 at front, degree of protection near terminal depends on installation

Connessioni
Accessories:
Clamp connection:  Cu 1.5-70mm² s(r), f+AE; lam. Cu 12x1-10; 3Nm torque
single wedge clamp terminal: Cu, Al* 16-70mm² s(r), s(s), f+AE; 3Nm torque
tunnel terminal 3x Cu 1.5-16mm² s(r), f+AE; 3Nm torque

*Connections not maintenance-free if aluminium conductors are used.

Miscellaneous 
For safe connection of the leads, the shock protection is split into 2. Self-closing inspection holes are available in the cover.

Brand 
Woehner or equivalent

Cod. art.
33222000