Text for specification

Descrizione
CRITO®60Classic
Piastra con morsetti di connessione, 3p
95 - 185 mm²
60Classic

Norme
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Valori elettrici
corrente nominale (IEC):	350 A
tensione nominale (IEC) AC:	690 V
corrente d'impiego max. (IEC):	460 A
tensione max. ammissibile (IEC) AC:	1000 V
tensione max. ammissibile (IEC) DC:	1500 V

resistenza nom. alla corrente di picco Ipk max.:	55,8 kA

Connessioni
für Anwendungen nach IEC / EN :
Cu und Al 95 - 185 mm² Rundleiter mehrdrähtig und Sektorleiter mehrdrähtig
Cu auch feindrähtig, direkt geklemmt

for applications acc. to IEC / EN:
Cu or Al 95 - 185mm², round stranded or sector-shaped stranded cables
also fine stranded Cu cables (direct clamping)   

Suitable for aluminium cables.
When using aluminium cables, observe the maintenance instructions.

Proprietà materiali
Corpo base:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Copertura:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free

Terminals: 	galvanised steel, chromited screw: 	hexagon socket screw, galvanised, chromited, thrust piece 	brass, nickel-plated

Miscellaneous 
Terminals with captive clamping screws
Conductor can be overlapped
Indication of nominal cross-section and tightening torque noted on the terminals.

Brand 
Woehner or equivalent

Cod. art.
01199000