Text for specification

Descrizione
QUADRON^®Panel
Base per fusibili NH 250 A, per pannello, per fotovoltaico
ingresso vite M10, uscita su barra 2x 30 x 10
Gr. NH 1XL / 1P, incl. protezione

Norme
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Omologazioni
UL

Valori elettrici
corrente nominale (IEC):	250 A
tensione nominale (IEC) AC:	1000 V
tensione nominale (IEC) DC:	1500 V

corrente nominale (UL):	250 A
tensione nominale (UL) DC:	1500 V

power dissipation at full load of the item:	5,5 W
tensione di picco U_imp:	6 kV
resistenza al corto circuito con protezione tramite fusibili:	50 kA

SCCR:	15 kA

for fuse links IEC 60269-6

Proprietà materiali
Corpo base:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contatti:
	spring-loaded copper contacts, silver plated 
Viti di collegamento:
	screw M10, galvanized, chromized
Protezione contro contatto accidentale:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Miscellaneous 
For one or two internal busbars 30x10mm.
Busbar fully shock protected by the contact cover.
The shock protection is split into 2.

Brand 
Woehner or equivalent

Cod. art.
03289000