Text for specification

Descrizione
Base sezion. verticale per fusibili NH, 160 A
vite M8 / brida 70mm²
Gr. NH 00
100Energy
185mm-System

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Omologazioni
IEC (CB), CCC

Valori elettrici
corrente nominale (IEC):	160 A
tensione nominale (IEC) AC:	800 V

AC22 B (690 V) 
AC23 B (400V)
AC23 B (500V / 125A) AC20 (800 V) Sichtbarer Hinweis notwendig: Nicht unter Last schalten in Fall von Betriebsspannung höher als 690 V   

DC-20B
max. voltage between the fuses: 1000V
visible information required: Do not switch under load.

power dissipation at full load of the item:	20,0 W

tensione nominale di isolamento Ui AC:	1000 V
tensione di picco Uimp:	8 kV
tensione max. ammissibile (IEC) DC:	1000 V

Degree of protection IP30 at front, degree of protection near terminal depends on installation

Connessioni
viti M8 : 
C. serr. 12 - 14 Nm

Proprietà materiali
Corpo base:
	resistenza alle temperature fino a 125°C, 
	ignifugo secondo UL 94, 
	tenuta alle correnti di fuga CTI 200
Contatti:
	spring-loaded copper contacts, silver plated 
Protezione contro contatto accidentale:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Coperchio:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Miscellaneous 
Self-closing inspection holes are available in the cover.

Brand 
Woehner or equivalent

Cod. art.
33235000