Text for specification

Descrizione
QUADRON^®Panel
Base per fusibili cilindr.
Class J / 3P, morsetti 70 mm²
100 A / 600 V (29 x 118)

Norme
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016, Fuse system H

Omologazioni
CSA, UL

Valori elettrici

corrente nominale (UL):	100 A
tensione nominale (UL) AC:	600 V
tensione nominale (UL) DC:	600 V

power dissipation at full load of the item:	2,5 W

SCCR:	200 kA

for Class J fuses 70 - 100A as per UL 248-8 (29x118)

Connessioni
tunnel terminal with hole of 12,5 mm diameter acc. to IEC / EN :
6 - 70 mm²
flexible cables, directly or with wire-end ferrule, 
solid and stranded round cables, 
Md 14 - 16 Nm

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

acc. to UL :
AWG 10 - AWG 2/0
stranded cables Class B acc. to UL 486E
125 - 142 lb.in. 

Proprietà materiali
Corpo base:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Protezione contro contatto accidentale:
	temperature stability 125°C,
	fire behaviour UL 94 HB,
	creepage resistance CTI 200,
	halogen-free 

Brand 
Woehner or equivalent

Cod. art.
33306000