Text for specification

Descrizione
QUADRON®Panel
Base per fusibili NH 250 A, per pannello, per fotovoltaico
ingresso vite M10, uscita su barra 2x 30 x 10, per inserimenti TA del tipo LEM HTA
Gr. NH 1XL / 1P, incl. protezione

Norme
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Valori elettrici
corrente nominale (IEC):	250 A
tensione nominale (IEC) AC:	1000 V
tensione nominale (IEC) DC:	1500 V

power dissipation at full load of the item:	5,5 W
tensione di picco Uimp:	6 kV
resistenza al corto circuito con protezione tramite fusibili:	50 kA

for fuse links IEC 60269-6

Connessioni
Connection screws for busbars: Hexagonal screw M10, length across flats 16, tightening torque 30Nm
connection width 25mm 
fastening to mounting plate: 2x 10.5mm hole, intended for hexagonal screw M10, tightening torque 5Nm

Miscellaneous 
For one or two internal busbars 30x10mm.
Busbar fully shock protected by the contact cover.
The shock protection is split into 2.

Brand 
Woehner or equivalent

Cod. art.
03288000