Text for specification

Descrizione
AMBUS^®Panel
Base sezion. per fusibili cilindr., per fus. extrarapidi
14 x 51 / 1P
50 A / 690 V

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Omologazioni
IEC (CB), CSA, UL, CCC

Valori elettrici
corrente nominale (IEC):	50 A
tensione nominale (IEC) AC:	690 V

corrente nominale (UL):	50 A
tensione nominale (UL) AC:	600 V
tensione nominale (UL) DC:	600 V

power dissipation at full load of the item:	0,9 W

tensione nominale di isolamento U_i AC:	800 V
tensione di picco U_imp:	6 kV

SCCR:	100 kA

for fuse links as per IEC / EN 60269-2 with permitted rated power dissipationsup to max. 5W for gG/gL
up to max. 3W for aM
for fuse links aR / gR / gRL under operating conditions up to max. 6.5W, for which at least 25mm² leads must be connected

Connessioni
morsetti a gabbia :
1,5 - 35 mm² / AWG 14 - AWG 2 
cavi flessibili, direttam. o con ferrula
C. serr. 2,5 - 3,0 Nm / 22 - 26 lb.in.

(cavi flessibili con ferrula potrebbero no più entrare, se scelti con sezione max.)

Miscellaneous 
large clamping range
 holder for label

Brand 
Woehner or equivalent

Cod. art.
31278000