Text for specification

Descrizione
AMBUS®Panel
Base sezion. per fusibili cilindr., con LED
Class J / 2P, morsetti 50 mm²
30 A / 600 V (21x57)

Norme
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016, Fuse system H

Omologazioni
CSA, UL

Valori elettrici

corrente nominale (UL):	30 A
tensione nominale (UL) AC:	600 V
tensione nominale (UL) DC:	600 V

power dissipation at full load of the item:	0,4 W

SCCR:	200 kA

for Class J fuses 1 - 30A as per UL 248-8 (21x57)

indicator light
operating voltage range: 110 - 600 V AC / DC

Connessioni
for applications acc. to IEC / EN :
1 wire : 
Cu 0,75 - 1,0 mm², Md 2,0 - 2,5 Nm / 18 - 22 lb.in.
Cu 1,5 - 50 mm², Md 3,5 - 4,0 Nm / 31 - 35 lb.in.
2 wires (of same cross-section) : 
Cu 0,75 - 1,0 mm², Md 2,0 - 2,5 Nm / 18 - 22 lb.in.
Cu 1,5 - 10 mm², Md 3,5 - 4,0 Nm / 31 - 35 lb.in.
flexible cables, directly or with wire-end ferrule
(flexible cables of max. cross-section may not fit when using wire-end ferrule)

for applications acc. to UL / CSA :
only Cu cables acc. to UL 486E 60°C/75°C
1 wire : 
AWG 18 - AWG 1, Class B, Md 3,5 - 4,0 Nm / 31 - 35 lb.in.
2 wires (of identical cross-section) : 
AWG 18 - AWG 8, Class B, Md 3,5 - 4,0 Nm / 31 - 35 lb.in.

Miscellaneous 
large clamping range, also for two identical conductors (adjacent)
holder for label
with indicator for tripped fuse
any polarity for DC voltage applications

Brand 
Woehner or equivalent

Cod. art.
31933000