Text for specification

Descrizione
AMBUS®Panel
Base sezion. per fusibili cilindr., con LED
14 x 51 / 1P
50 A / 110 - 690 V

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Omologazioni
CSA, UL, CCC

Valori elettrici
corrente nominale (IEC):	50 A
tensione nominale (IEC) AC:	690 V

corrente nominale (UL):	50 A
tensione nominale (UL) AC:	600 V
tensione nominale (UL) DC:	600 V

power dissipation at full load of the item:	0,9 W

tensione nominale di isolamento Ui AC:	690 V
tensione di picco Uimp:	6 kV
tensione max. ammissibile (IEC) AC:	725 V

SCCR:	100 kA

for fuse links as per IEC / EN 60269-2 with permitted rated power dissipations
up to max. 5W for gG/gL 
up to max. 3W for aM

indicator light
operating voltage range: 110 - 690V AC / DC

Connessioni
morsetti a gabbia :
1,5 - 35 mm² / AWG 14 - AWG 2 
cavi flessibili, direttam. o con ferrula
C. serr. 2,5 - 3,0 Nm / 22 - 26 lb.in.

(cavi flessibili con ferrula potrebbero no più entrare, se scelti con sezione max.)

Proprietà materiali
Corpo base:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Portafusibile:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
	
Viti di collegamento:
	screw +/- (PZ2), galvanized, chromized 

Miscellaneous 
large clamping range
holder for label
with indicator for tripped fuse
any polarity for DC voltage

Brand 
Woehner or equivalent

Cod. art.
31135000