Text for specification

Descrizione
CAPUS®Panel
Sezionatore sottocarico, 3poli + N
morsetti a gabbia 50 - 70 mm² / AWG 1 - 3/0, manovra giallo -rosso
125 A

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Omologazioni
UL

Valori elettrici
corrente nominale (IEC):	125 A
tensione nominale (IEC) AC:	690 V

corrente nominale (UL):	125 A
tensione nominale (UL) AC:	600 V

AC-23 A (690 V / 125 A)
AC-22 A (690 V / 125 A)
AC-21 A (690 V / 125 A)

power dissipation at full load of the item:	10,0 W

tensione nominale di isolamento Ui AC:	800 V
tensione di picco Uimp:	6 kV
potere nominale di chiusura:	4,5 kA

Connessioni
cage clamp connection
screw drive: S4 
wire stripping: 15 mm
min. cross-section: 50 mm²
max. cross-section: 70 mm²
cage clamp connection
screw drive: S4 
wire stripping: 15 mm
min. cross-section: 50 mm²
max. cross-section: 70 mm²
rm: 50 - 70 mm²
f: 50 - 70 mm²
f + AE: 50 - 70 mm²
(f + AE may not fit with max. cross-section) 
Md min.: 6,0 Nm
Md max.: 6,0 Nm
Not suitable for aluminium cables !

min. cross-section UL: AWG 6 
max. cross-section UL: AWG 3/0 
torque (UL): 53,1 lb-in
for wires UL: Cu 75°C 

Miscellaneous 
lockable in 0-position with a padlock (max. 5 mm diameter) 

Brand 
Woehner or equivalent

Cod. art.
33037000A