Text for specification

Descrizione
QUADRON^®60Classic
base sezion. per fus. NH00 160 A, per barre, uscita in basso / alto
vite M8
60Classic

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Omologazioni
IEC (CB), UL, VDE, CCC

Valori elettrici
corrente nominale (IEC):	160 A
tensione nominale (IEC) AC:	690 V
tensione nominale (IEC) DC:	440 V

corrente nominale (UL):	160 A
tensione nominale (UL) AC:	600 V

AC-21B (690V)
AC-22B (500V)
AC-20B (1000V) at pollution degree 2

visible information required if used at more than 690V AC: do not switch under load

DC specifications: 2 current paths (L1,L3) in series
DC-21B (220V)
DC-21B (440V/100A)
DC-22B (220V/63A)
DC-20B (1000V) at pollution degree 2

visible information required if used at more than 440V DC: do not switch under load

power dissipation at full load of the item:	17,7 W

tensione nominale di isolamento U_i AC:	800 V
tensione di picco U_imp:	6 kV
tensione max. ammissibile (IEC) DC:	800 V

SCCR:	100 kA

In accordance with the specified AC and DC switching properties and in consideration of the overload conditions, certain distances to earthed metal parts are to be adhered to. detailed information upon inquiry

When several devices are used side-by-side in continuous operation, the rated load factor specified in IEC / EN 61439-1, Table 1, must be observed.

System component: degree of protection IP30 at front as per DIN EN 60529, degree of protection near terminal depends on installation
adapter module: front side degree of protection IP20 as per DIN EN 60529 (finger-safe)

Proprietà materiali
Corpo base:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Protezione contro contatto accidentale:
	resistenza alle temperature fino a 125°C, 
	ignifugo secondo UL 94, 
	tenuta alle correnti di fuga CTI 200
Coperchio:
	resistenza alle temperature fino a 125°C, 
	ignifugo secondo UL 94, 
	tenuta alle correnti di fuga CTI 200
Piastra adattatore:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contatti:
	spring-loaded copper contacts, silver plated 
Viti di collegamento:
	screw M8, galvanized, chromized

Miscellaneous 
CrossLink® adapter technology
Fast and safe conversion of the connection for top or bottom; the parts under voltage remain shock protected
Simple and safe clicking into place and making contact
Safe connection through shock protection split into 2
Busbar supports for flat busbars can be mounted above each other

Brand 
Woehner or equivalent

Cod. art.
33398000