Text for specification

Descrizione
connessione longitudinale
60 mm
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Norme
IEC 61439-1:2011

Omologazioni
UL

Valori elettrici
tensione nominale (IEC) AC:	690 V

corrente nominale (UL):	1.100 A
tensione nominale (UL) AC:	1000 V
tensione nominale (UL) DC:	1000 V
corrente d'impiego max. (IEC):	1.000 A
tensione max. ammissibile (IEC) AC:	1000 V
tensione max. ammissibile (IEC) DC:	1500 V

the busbar connector was tested in an arrangment where the busbar supports at the connection of the 2 systems had a spacing of 200 mm

test conditions: 120x10 - 120x10 (2x 01481)
peak withstand current Ipk: 109 kA
Icw (1,0 s): 51 kA

test conditions: 100x10 - 100x10 (1x 01480 + 1x 01481)
peak withstand current Ipk: 106 kA
Icw (1,0 s): 50 kA

test conditions: 60x10 - 60x10 (1x 01481)
peak withstand current Ipk: 81 kA
Icw (1,0 s): 34 kA

Brand 
Woehner or equivalent

Cod. art.
01481000A