Text for specification

Descrizione
AMBUS^®Panel
Base sezion. per fusibili cilindr., per fus. extrarapidi
22 x 58 / 2P
100 A / 690 V

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Omologazioni
IEC (CB), CSA, UL, CCC

Valori elettrici
corrente nominale (IEC):	100 A
tensione nominale (IEC) AC:	690 V

corrente nominale (UL):	80 A
tensione nominale (UL) AC:	600 V
tensione nominale (UL) DC:	600 V

power dissipation at full load of the item:	7,0 W

tensione nominale di isolamento U_i AC:	800 V
tensione di picco U_imp:	6 kV

SCCR:	100 kA

for fuse links as per IEC / EN 60269-2 with permitted rated power dissipationsup to max. 9.5W for gG/gL up to max. 7W for aMfor fuse links aR / gR / gRL under operating conditions up to max. 11W, for which at least 50mm² leads must be connected

Connessioni
morsetti a gabbia :
4 - 50 mm² / AWG 10 - AWG 1/0 
cavi flessibili, direttam. o con ferrula
C. serr. 3,5 - 4,0 Nm / 31 - 35 lb.in.

(cavi flessibili con ferrula potrebbero no più entrare, se scelti con sezione max.)

Miscellaneous 
large clamping range

Brand 
Woehner or equivalent

Cod. art.
31282000