Text for specification

Descrizione
EQUES®185Power
Adattatore 1200 A 
300 x 652, coll.al sistema in basso, mont.su barre non forate, fasi invertite
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Norme
IEC 61439-1:2020

Omologazioni
UL

Valori elettrici
corrente nominale (IEC):	1.200 A
tensione nominale (IEC) AC:	690 V
tensione nominale (IEC) DC:	800 V

corrente nominale (UL):	1.200 A
tensione nominale (UL) AC:	1000 V

power dissipation at full load of the item:	365,0 W

tensione nominale di isolamento Ui AC:	1000 V
tensione di picco Uimp:	12 kV

resistenza nom. alla corrente di picco Ipk max.:	106 kA

mit Eaton NZM4 1250A bis 1200A einsetzbar!

Brand 
Woehner or equivalent

Cod. art.
32788000A