Text for specification

Descrizione
QUADRON®60Classic
base sezion. per fus. NH000, 125 A, per barre, uscita in basso / alto
morsetti a gabbia
60Classic

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Omologazioni
IEC (CB), UL, CCC

Valori elettrici
corrente nominale (IEC):	125 A
tensione nominale (IEC) AC:	690 V
tensione nominale (IEC) DC:	440 V

corrente nominale (UL):	125 A
tensione nominale (UL) AC:	600 V

AC-23B (400 V)
AC-22B (500 V)
AC-21B (690 V)

DC specifications: 2 current paths (L1,L3) in series 
DC-22B (440V/63A)
DC-22B (220V/100A)
DC-21B (440V/80A)
DC-21B (220V/125A)

power dissipation at full load of the item:	10,5 W

tensione nominale di isolamento Ui AC:	800 V
tensione di picco Uimp:	6 kV
tensione max. ammissibile (IEC) DC:	800 V

SCCR:	100 kA

In accordance with the specified AC and DC switching properties and in consideration of the overload conditions, certain distances to earthed metal parts are to be adhered to. detailed information upon inquiry

When several devices are used side-by-side in continuous operation, the rated load factor specified in IEC / EN 61439-1, Table 1, must be observed.

Degree of protection IP30 at front, degree of protection near terminal depends on installation

Connessioni
Box terminal:
2.5 -50mm² flexible cables, 
1.5 -50mm² flexible cables with wire-end ferrules 
1.5 - 10mm² solid round
16 - 50mm² stranded round 
(flexible cables of maximum cross-section may not fit when using wire-end ferrule)
lam. Cu. 6-9 mm wide 
Terminal space 10mm x 10mm

Miscellaneous 
Self-closing inspection holes are available in the cover.

Brand 
Woehner or equivalent

Cod. art.
33216000