Text for specification

Descrizione
Base sezion. verticale per fusibili NH, 160 A
vite M8 / brida 70mm², con segnalaz. Intervento fusibili
Gr. NH 00
100Energy
185mm-System

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Omologazioni
IEC (CB), CCC

Valori elettrici
corrente nominale (IEC):	160 A
tensione nominale (IEC) AC:	400 V

AC-23B (400V)

power dissipation at full load of the item:	20,0 W

tensione nominale di isolamento Ui AC:	400 V
tensione di picco Uimp:	4 kV

Electronic fuse monitoring:
nominal voltage: 3AC 400V,
nominal frequency: 50...40Hz,
switch contact: 2 changeover switches, max. AC 250V, AC15  closer 3A, opener 1A,
rated surge voltage: 4kV,
pollution degree: 2

Degree of protection IP30 at front, degree of protection near terminal depends on installation

Connessioni
viti M8 : 
C. serr. 12 - 14 Nm

Miscellaneous 
Self-closing inspection holes are available in the cover.
Electronic fuse monitoring:
operating current principle, optionally with latching properties (latches without bridge X1-X2)
device display:
green LED = intact fuses
red LED = fuse tripped, cover position up

Brand 
Woehner or equivalent

Cod. art.
33286000