Text for specification

Descrizione
SECUR®60Classic EasyLiner
base D0 sezionabile 3p, per sistemi barre 3p
per fusibili D01 e D02
E18 / 63 A / 3P
60Classic

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Omologazioni
IEC (CB), VDE, CCC

Valori elettrici
Corrente nominale (IEC):	63 A
tensione nominale (IEC) AC:	400 V

AC-22B (400 V)

power dissipation at full load of the item:	7,0 W

tensione nominale di isolamento Ui AC:	500 V
tensione di picco Uimp:	6 kV

reduction factor at ambient temperature:
35°C     1,0
45°C     0,9
55°C     0,8

for fuse links and gauge elements acc. to IEC / HD 60269-3

use of D02 fuse links with silver plated caps is recommended

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard. 

Connessioni
1,5 - 16 mm² round stranded and flexible without wire-end ferrule
1,5 - 16 mm²  flexible with wire-end ferrule*
1,5 - 10 mm²  flexible with wire-end ferrule
1,5 - 10 mm² round solid

* 16 mm² prepared with crimping tool PZ 16 (Weidmüller) or
with jointing clamp Crimpfox 25R (Phoenix Contact)

the connecting wires can be placed at the side : 
up to 6mm² without side module
up to 10mm² when using  the side module

Proprietà materiali
Involucro:
	temperature stability 130°C,
	self-extinguishing in acc. to UL 94,
	creepage resistance CTI 600,
	halogen-free 
Levetta di manovra:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Miscellaneous 
spring terminal enables connection without tools (at first installation)

Brand 
Woehner or equivalent

Cod. art.
31574000B