Text for specification

Descrizione
CRITO^®
Morsetto a pinza
Cu / Al 95 - 300 mm²
60Classic
100Energy
185mm-System
centre feed unit

Norme
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Omologazioni
CSA, UL

Valori elettrici
Corrente nominale (IEC):	500 A
tensione nominale (IEC) AC:	690 V

corrente nominale (UL):	420 A
tensione nominale (UL) AC:	600 V
Utilizzabile fino a max. (IEC):	600 A
tensione max. ammissibile (IEC) AC:	1000 V
tensione max. ammissibile (IEC) DC:	1500 V

resistenza nom. alla corrente di picco I_pk max.:	81,4 kA

SCCR:	65 kA

Connessioni
for applications acc. to IEC / EN :
Cu 95 - 300 mm² stranded round cables and stranded sectored cables as well as flexible cables (directly)
Cu 240 - 300 mm² fine stranded flexible cables (directly)
Al 120 - 300 mm² stranded round cables and stranded sectored cables
Al 120 - 240 mm² solid sectored cables

for applications acc. to UL / CSA :
Cu 95 - 300 mm² / AWG 3/0 - MCM 600

Suitable for aluminium cables.
When using aluminium cables, observe the maintenance instructions.

Brand 
Woehner or equivalent

Cod. art.
01760000