Text for specification

Descrizione
SECUR®Panel
Sezionatore per fusibili D0 fino a 63 A
con LED
1P

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Omologazioni
VDE

Valori elettrici
Corrente nominale (IEC):	63 A
tensione nominale (IEC) AC:	400 V
tensione nominale (IEC) DC:	65 V

AC-22B (400V)

 DC-22B (65 V)

power dissipation at full load of the item:	2,6 W

tensione nominale di isolamento Ui AC:	500 V
tensione di picco Uimp:	6 kV

for fuse links and gauge rings as per DIN VDE 0636-3 IEC / HD 60269-3
utilisation category as per VDE 0638: AC-22 (400V)

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard.

There is a transfer of the potential from the busbars, through the LED units, to the terminals  when the fuse links are removed and the switching mechanismn is closed. 

Miscellaneous 
Double function terminal
any feed direction
captive fuse-carrier
sealable operation

Brand 
Woehner or equivalent

Cod. art.
31556000A