Text for specification

Descrizione
SECUR®60Classic PowerLiner
sezionatore per fusibili 10x38, montaggio su barre
per fusibili 10x38 sec. IEC 60269-2
3P
60Classic

Norme
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Valori elettrici
Corrente nominale (IEC):	32 A
tensione nominale (IEC) AC:	690 V
tensione nominale (IEC) DC:	110 V

AC-23A (400 V)
AC-22A (690 V) 

power dissipation at full load of the item:	5,3 W

tensione nominale di isolamento Ui AC:	500 V
tensione di picco Uimp:	6 kV
tensione max. ammissibile (IEC) AC:	725 V

for fuse links gG and aM as per IEC / EN 60269-2

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard. 

Proprietà materiali
Involucro:
	resistenza alle temperature fino a 140°C,
	ignifugo secondo UL 94, 
	tenuta alle correnti di fuga CTI 225,
	Senza silicio, senza alogeni
Levetta di manovra:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200
Portafusibile:
	temperature stability 150°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 125,
	halogen-free
Copertura:
	temperature stability 125°C,
	fire behaviour UL 94 HB,
	creepage resistance CTI 200,
	halogen-free 
Viti di collegamento:
	screw +/- (PZ2), galvanized, chromized 

Brand 
Woehner or equivalent

Cod. art.
31232000