Text for specification

Description
TRITON^®Panel
base fusível D0, montagem em painel
E 14 / 16 A / 3P
proteção contra contato cf. DGUV V3

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-3:2010 + A1:2013 + A2:2019

Approvals
CCC

Electrical data
Corrente de medição (IEC):	16 A
Tensão de medição (IEC) AC:	400 V
Tensão de medição (IEC) DC:	250 V

power dissipation at full load of the item:	1,2 W
Tensão suportável nominal de impulso Uimp:	6 kV
tensão máxima IEC AC:	440 V
tensão máxima IEC DC:	262 V
short-circuit strength when protected by fuses:	50 kA

A direção da alimentação marcada no produto deve ser rigorosamente observada. 

pontos terminais
box terminal :
1,5 - 35 mm² flexible cables, directly or with wire-end ferrule,
1,5 - 10 mm² solid round cables
Md 4,0 Nm

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Material properties
Body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Connecting screws:
	screw +/- (PZ2), galvanized, chromized 

Miscellaneous 
large clamping range, holder for label

Brand 
Woehner or equivalent

Nº da peça
31288000