Text for specification

Description
AMBUS®Panel
suporte para fusíveis cilíndricos
Class CC / 3P
30 A / 600 V

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016, Fuse system J

Approvals
CSA, UL, CCC

Electrical data

rated current (UL):	30 A
rated voltage (UL) AC:	600 V
rated voltage (UL) DC:	600 V

power dissipation at full load of the item:	0,9 W

SCCR:	200 kA

pontos terminais
for applications acc. to IEC / EN :
1 wire : 
Cu 0,75 - 25 mm²
2 wires (of same cross-section) :
Cu 0,75 - 10 mm² 
flexible cables, directly or with wire-end ferrule
(flexible cables of max. cross-section may not fit when using wire-end ferrule)
Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

for applications acc. to UL / CSA :
only Cu cables acc. to UL 486E 60°C/75°C
1 wire : 
AWG 18 - AWG 8, Class B, Md 2,0 -2,5 Nm / 18 - 22 lb.in.
AWG 6 - AWG 4, Class C, Md 2,5 - 3,0 Nm / 22 - 26 lb.in.
2 wires (of identical cross-section) : 
AWG 18 - AWG 8, Class B, Md 2,0 - 2,5 Nm / 18 - 22 lb.in. 
AWG 6, Class C, Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

Material properties
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Fuse-carrier:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
	
Connecting screws:
	screw +/- (PZ2), galvanized, chromized 

Miscellaneous 
large clamping range, also for two identical conductors (adjacent)
holder for label

Brand 
Woehner or equivalent

Nº da peça
31297000