Text for specification

Description
EQUES®185Power
adaptador para barramentos 1400 A
300 x 652, conexão inferior, conexão por parafuso, fase alterada
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Standards
IEC 61439-1:2011

Approvals
UL

Electrical data
Corrente de medição (IEC):	1.400 A
Tensão de medição (IEC) AC:	690 V
Tensão de medição (IEC) DC:	800 V

rated current (UL):	1.200 A
rated voltage (UL) AC:	1000 V

power dissipation at full load of the item:	417,0 W

Tensão nominal de isolamento:	1000 V
Tensão suportável nominal de impulso Uimp:	12 kV

rated peak withstand current  Ipk max.:	106 kA

mit Schneider Electric NS1600 bis 1400A einsetzbar!

Brand 
Woehner or equivalent

Nº da peça
32720000A