Text for specification

Description
EQUES®185Power
adaptador para barramentos 1500A
300 x 652, conexão inferior, conexão de fixação
185Power

The 185Power is an innovative and powerful busbar system for professional energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnector, NH-switch-disconnector-fuses and adapters for circuit breakers.

Easy design of touch-safe busbar system by using Crosslink touch-safe protection covers.

Crosslink touch-safe protection cover with protection class IP2X front.
Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

Safe and fast drill-free mounting by terminal clamps of all system components on Crosslink touch-safe protection modules.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Standards
IEC 61439-1:2011

Approvals
UL

Electrical data
Corrente de medição (IEC):	1.500 A
Tensão de medição (IEC) AC:	690 V
Tensão de medição (IEC) DC:	800 V

rated current (UL):	1.200 A
rated voltage (UL) AC:	1000 V

power dissipation at full load of the item:	594,0 W

Tensão nominal de isolamento:	1000 V
Tensão suportável nominal de impulso Uimp:	12 kV

rated peak withstand current  Ipk max.:	106 kA

with Socomec Sirco 1250 A (Socomec no.26003U21) and 1600 A (Socomec no.26003U61) usable up to 1550 A
maximum 300 switching cycles

Brand 
Woehner or equivalent

Nº da peça
32764000A