Text for specification

Description
chave seccionadora de fusível vertical 160 A
parafuso M8/grampo 70 mm²
tamanho 00
60Classic

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
IEC (CB), CCC

Electrical data
Corrente de medição (IEC):	160 A
Tensão de medição (IEC) AC:	690 V

AC-22B (690V)
AC-23B (400V)
AC-23B (500V/125A)

DC-20B
max. voltage between the fuses: 1000V
visible information required: Do not switch under load.

power dissipation at full load of the item:	27,0 W

Tensão nominal de isolamento:	1000 V
Tensão suportável nominal de impulso Uimp:	8 kV
tensão máxima IEC DC:	1000 V

Degree of protection IP30 at front, degree of protection near terminal depends on installation

pontos terminais
screw M8 : 
Md 12 - 14 Nm

Material properties
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200
Contacts:
	spring-loaded copper contacts, silver plated 
Shock protection cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Handle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Miscellaneous 
Self-closing inspection holes are available in the cover.

Brand 
Woehner or equivalent

Nº da peça
33234000