Text for specification

Description
QUADRON®60Classic
porta-fusível montado no barramento Class J, conexão superior / inferior
para ligações com fusíveis Class J 225 - 400 A (54x181)
3P, com prensa-cabo
60Classic

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016, Fuse system H

Approvals
CSA, UL

Electrical data

rated current (UL):	400 A
rated voltage (UL) AC:	600 V
rated voltage (UL) DC:	600 V

power dissipation at full load of the item:	46,8 W

SCCR:	65 kA

pontos terminais
tunnel terminal with hole of 23,0 mm diameter

acc. to IEC / EN :
16 - 240 (300) mm²
flexible cables, directly or with wire-end ferrule, 
solid and stranded round cables, 
Md 38 - 40 Nm

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

acc. to UL :
AWG 4 - MCM 600
stranded cables Class B acc. to UL 486E
336 - 355 lb.in.

Material properties
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Shock protection cover:
	temperature stability 125°C,
	fire behaviour UL 94 HB,
	creepage resistance CTI 200,
	halogen-free 
Connecting screws:
	screw M12, galvanized, chromized

Miscellaneous 
the product is based on the UL approval in category IZLT2 also listed in category NMTR (file E123577)

Brand 
Woehner or equivalent

Nº da peça
33311000