Text for specification

Description
CRITO®60Classic
placa terminal de conexão, 3 polos
10 - 120 mm², AWG 6 - 250 MCM, lam. Cu. 9 - 15.5 x 2,4 - 10
60Classic

Standards
IEC 61439-1:2020
IEC 60999-1:1999
IEC 60999-2:2003

Approvals
CSA, UL

Electrical data
Corrente de medição (IEC):	250 A
Tensão de medição (IEC) AC:	690 V

corrente nominal (UL):	250 A
rated voltage (UL) AC:	600 V

power dissipation at full load of the item:	6,0 W
current capacity (IEC) max.:	440 A
Tensão suportável nominal de impulso Uimp:	6 kV
tensão máxima IEC AC:	1000 V
tensão máxima IEC DC:	1500 V

rated peak withstand current  Ipk max.:	56,3 kA

SCCR: 100 kA with JDDZ fuse Class J 500 A / 600 V AC, 35 kA with any DIVQ/7 circuit breaker 600 A / 600 V AC, 50 kA with any DIVQ/7 circuit breaker 600 A / 480 V AC, 65 kA with any DIVQ/7 circuit breaker 400 A / 480 V AC, 100 kA with JDDZ fuse Class J 600 A / 480 V AC 

Miscellaneous 
Terminals can be removed for connection of uncut conductors

Brand 
Woehner or equivalent

Nº da peça
01243000