Text for specification

Description
CRITO^®60Classic
conjunto de conexão, 3 polos, sem cobertura
95 -  300 mm², AWG 3/0 - 600 MCM
60Classic

Standards
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Approvals
CSA, UL

Electrical data
Corrente de medição (IEC):	500 A
Tensão de medição (IEC) AC:	690 V

rated current (UL):	420 A
rated voltage (UL) AC:	600 V
current capacity (IEC) max.:	560 A
tensão máxima IEC AC:	1000 V
tensão máxima IEC DC:	1500 V

rated peak withstand current  I_pk max.:	67,2 kA

SCCR: 65 kA with any DIVQ/7 circuit breaker 400 A / 480 V AC, 35 kA with any DIVQ/7 circuit breaker 400 A / 600 V AC, 200 kA with fuse JDDZ Class J 600 A / 600 V AC, 200 kA with JDDZ fuse Class L 800 A / 600 V AC, 100 kA with JDDZ fuse Class L 1200 A / 600 V AC 

pontos terminais
for applications acc. to IEC / EN :
Cu 95 - 300 mm² stranded round cables and stranded sectored cables as well as flexible cables (directly)
Cu 240 - 300 mm² fine stranded flexible cables (directly)
Al 120 - 300 mm² stranded round cables and stranded sectored cables
Al 120 - 240 mm² solid sectored cables

for applications acc. to UL / CSA :
Cu 95 - 300 mm² / AWG 3/0 - MCM 600

Suitable for aluminium cables.
When using aluminium cables, observe the maintenance instructions.

Brand 
Woehner or equivalent

Nº da peça
01537000