Text for specification

Description
chave seccionadora de fusível vertical 160 A
parafuso M8 / braçadeira 70 mm2, com monitoramento eletrônico de fusível  
tamanho 00
60Classic

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
IEC (CB), CCC

Electrical data
Corrente de medição (IEC):	160 A
Tensão de medição (IEC) AC:	400 V

AC-23B (400V)

power dissipation at full load of the item:	20,0 W

Tensão nominal de isolamento:	400 V
Tensão suportável nominal de impulso Uimp:	4 kV

Electronic fuse monitoring:
nominal voltage: 3AC 400V,
nominal frequency: 50...40Hz,
switch contact: 2 changeover switches, max. AC 250V, AC15  closer 3A, opener 1A,
rated surge voltage: 4kV,
pollution degree: 2

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

Degree of protection IP30 at front, degree of protection near terminal depends on installation

pontos terminais
screw M8 : 
Md 12 - 14 Nm

Miscellaneous 
Self-closing inspection holes are available in the cover.
Electronic fuse monitoring:
operating current principle, optionally with latching properties (latches without bridge X1-X2)
device display:
green LED = intact fuses
red LED = fuse tripped, cover position up

Brand 
Woehner or equivalent

Nº da peça
33285000