Text for specification

Description
isolamento do sistema, traseiro
conjunto para suporte de barramento distancia 700 mm (centro a centro)
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Standards
IEC 61439-1:2011

Approvals
UL

Electrical data

Material properties
Cover:
	temperature stability 125°C,
	self-extinguishing in acc. to UL 94,
	creepage resistance CTI 600,
	halogen-free

Miscellaneous 
To safeguard against touching the busbars from behind.

Brand 
Woehner or equivalent

Nº da peça
01436000A