Text for specification

Description
conector longitudinal de barras
40 mm
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Standards
IEC 61439-1:2011

Approvals
UL

Electrical data
Tensão de medição (IEC) AC:	690 V

rated current (UL):	700 A
rated voltage (UL) AC:	1000 V
rated voltage (UL) DC:	1000 V
current capacity (IEC) max.:	750 A
tensão máxima IEC AC:	1000 V
tensão máxima IEC DC:	1500 V

the busbar connector was tested in an arrangment where the busbar supports at the connection of the 2 systems had a spacing of 200 mm

test conditions: 100x10 - 100x10 (1x 01480 + 1x 01481)
peak withstand current Ipk: 106 kA
Icw (1,0 s): 50 kA

test conditions: 80x10 - 80x10 (2x 01480)
peak withstand current Ipk: 106 kA
Icw (1,0 s): 50 kA

test conditions: 40x10 - 40x10 (1x 01480)
peak withstand current Ipk: 81 kA
Icw (1,0 s): 34 kA

test conditions: 30x10 - 30x10 (1x 01480)
peak withstand current Ipk: 81 kA
Icw (1,0 s): 34 kA

Material properties
Screws:
	Hexagon screw M10, length across flats 16
Terminal body:
	Cu-ETP R300 (EN 13601), tinned

Brand 
Woehner or equivalent

Nº da peça
01480000A