Text for specification

Description
QUADRON®Panel
base fusível NH 630 A, montagem em painel
ambos os lados parafusos M12
tamanho 3 / 3P, com proteção contra toque

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Electrical data
Corrente de medição (IEC):	630 A
Tensão de medição (IEC) AC:	690 V
Tensão de medição (IEC) DC:	440 V

power dissipation at full load of the item:	90,0 W
Tensão suportável nominal de impulso Uimp:	6 kV
tensão máxima IEC AC:	800 V
tensão máxima IEC DC:	800 V
short-circuit strength when protected by fuses:	50 kA

for fuse links IEC 60269-2 / DIN VDE 0636-201 size 3 up to 60W power dissipation

Material properties
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 
Shock protection cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Brand 
Woehner or equivalent

Nº da peça
03769000