Text for specification

Description
SECUR®60Classic EasyLiner
seccionador-interruptor-fusível D0 em barramento 5 polos
Para fusíveis D01 e D02, para sistemas de barramento 250 A, 400 A e 630 A da empresa Hensel
E18 / 63 A / 3P
60Classic

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
IEC (CB), VDE, CCC

Electrical data
Corrente de medição (IEC):	63 A
Tensão de medição (IEC) AC:	400 V

AC-22B (400 V)

power dissipation at full load of the item:	7,0 W

Tensão nominal de isolamento:	500 V
Tensão suportável nominal de impulso Uimp:	6 kV

reduction factor at ambient temperature:
 35°C     1,0
 45°C     0,9
 55°C     0,8

for fuse links and gauge elements acc. to IEC / HD 60269-3

 use of D02 fuse links with silver plated caps is recommended

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard. 

pontos terminais
1,5 - 16 mm² round stranded and flexible without wire-end ferrule
1,5 - 16 mm²  flexible with wire-end ferrule*
1,5 - 10 mm²  flexible with wire-end ferrule
1,5 - 10 mm² round solid

* 16 mm² prepared with crimping tool PZ 16 (Weidmüller) or
with jointing clamp Crimpfox 25R (Phoenix Contact)

the connecting wires can be placed at the side :
up to 6mm² without side module
up to 10mm² when using  the side module

Miscellaneous 
spring terminal enables connection without tools (at first installation)

Brand 
Woehner or equivalent

Nº da peça
31588000A