Text for specification

Description
AMBUS®60Classic
porta-fusível montado no barramento Class J, conexão inferior
para ligações com fusíveis Class J 35 - 60 A (27x60), com LED
3P, solução completa baseada em adaptador para barramentos
60Classic

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016, Fuse system H

Approvals
CSA, UL

Electrical data

rated current (UL):	60 A
rated voltage (UL) AC:	600 V
rated voltage (UL) DC:	600 V

power dissipation at full load of the item:	10,7 W

SCCR:	100 kA

pontos terminais
for applications acc. to IEC / EN :
1 wire : Cu 6 - 50 mm², Md 3,5 - 4,0 Nm / 31 - 35 lb.in.
2 wires (of same cross-section) : Cu 6 - 16 mm², Md 3,5 - 4,0 Nm / 31 - 35 lb.in.
flexible cables, directly or with wire-end ferrule
(flexible cables of max. cross-section may not fit when using wire-end ferrule)

for applications acc. to UL / CSA :
only Cu cables acc. to UL 486E
1 wire : AWG 14 - AWG 1, Class C, Md 4,0 Nm / 35 lb.in.
2 wires (of identical cross-section) :  AWG 14 - AWG 6, Class C, Md 4,0 Nm / 35 lb.in.

Material properties
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Adapter plate:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Fuse-carrier:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
	
Connecting screws:
	screw +/- (PZ2), galvanized, chromized 

Brand 
Woehner or equivalent

Nº da peça
31970000