Text for specification

Description
QUADRON®60Classic
chave seccion. de fusível NH, tam. 1, 250 A, p/ mont. em barramento, conexão sup / inf
parafuso M10
60Classic

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
IEC (CB), UL, VDE, CCC

Electrical data
Corrente de medição (IEC):	250 A
Tensão de medição (IEC) AC:	690 V
Tensão de medição (IEC) DC:	250 V

rated current (UL):	250 A
rated voltage (UL) AC:	600 V

AC-22B (400V)
AC-23B (400V/160A)
AC-21B (690V)

to obtain a higher utilisation category the product can be retrofitted with arcing chambers (see accessories)

DC specifications: 2 current paths (L1,L3) in series
DC-20B (250V)

power dissipation at full load of the item:	26,0 W

Tensão nominal de isolamento:	800 V
Tensão suportável nominal de impulso Uimp:	6 kV
tensão máxima IEC AC:	725 V
tensão máxima IEC DC:	262 V

rated peak withstand current  Ipk max.:	13,7 kA

SCCR:	100 kA

for fuse links IEC 60269-2-1 (I) / DIN VDE 0636-201 size 1 up to 23W power dissipation, with grip lugs under voltage

Entsprechend den angegeben AC- und DC- Schalteigenschaften und unter Berücksichtigung der Überlastbedingungen, sind gewisse Abstände zu geerdeten Metallteilen einzuhalten. Nähere Informationen auf Anfrage.
Bei Verwendung als Trennschalter ist die Einhaltung der Abstände nicht erforderlich.

Degree of protection IP30 at front, degree of protection near terminal depends on installation

fuse monitoring:
rated operating voltage
AC 24-690V, DC 24-250V
potential-free opener and closer:
AC-15 24V/2A, (230V* 0.5A)
DC-13 24V/1A, 60V 0.15A

*pollution degree 2, surge category II
auxiliary energy not required,
for further information, see assembly manual

Material properties
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Shock protection cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200
Handle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Adapter plate:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 
Connecting screws:
	screw M10, galvanized, chromized

Miscellaneous 
CrossLink® adapter technology
Fast and safe conversion of the connection for top or bottom; the parts under voltage remain shock protected
Simple and safe clicking into place and making contact
Safe connection through shock protection split into two
Busbar supports for flat busbars can be mounted above each other
Self-closing test holes are available in the cover.

Brand 
Woehner or equivalent

Nº da peça
33160000