Text for specification

Description
AMBUS®Panel
suporte para fusíveis cilíndricos, com LED
Class CC / 3P
30 A / 600 V

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016, Fuse system J

Approvals
CSA, UL, CCC

Electrical data

rated current (UL):	30 A
rated voltage (UL) AC:	600 V
rated voltage (UL) DC:	600 V

power dissipation at full load of the item:	0,9 W

SCCR:	200 kA

indicator light
operating voltage range: 110 - 600 V AC / DC

pontos terminais
for applications acc. to IEC / EN :
1 wire : 
Cu 0,75 - 25 mm²
2 wires (of same cross-section) :
Cu 0,75 - 10 mm² 
flexible cables, directly or with wire-end ferrule
(flexible cables of max. cross-section may not fit when using wire-end ferrule)
Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

for applications acc. to UL / CSA :
only Cu cables acc. to UL 486E 60°C/75°C
1 wire : 
AWG 18 - AWG 8, Class B, Md 2,0 -2,5 Nm / 18 - 22 lb.in.
AWG 6 - AWG 4, Class C, Md 2,5 - 3,0 Nm / 22 - 26 lb.in.
2 wires (of identical cross-section) : 
AWG 18 - AWG 8, Class B, Md 2,0 - 2,5 Nm / 18 - 22 lb.in. 
AWG 6, Class C, Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

Miscellaneous 
large clamping range, also for two identical conductors (adjacent)
holder for label
with indicator for tripped fuse
any polarity for DC voltage

Brand 
Woehner or equivalent

Nº da peça
31300000